GT-800E TCS-3000

STATE-DRIVEN TURBINE TRAINER

STARTUP / SHUTDOWN SEQUENCE TABLE

Normal Mode vs Demo Mode (30% faster)  |  57 MW ISO  |  6600 RPM Core / 1500 RPM Gen  |  Natural Gas (DLE)

# PHASE 1 — EQUIPMENT PREPARATION (Pre-Start)

| STEP | EQUIPMENT | TAG | ACTION | NORMAL | DEMO | PROCESS RESPONSE |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | LO Pump A (Main) | LOP-01 | START | 18.0 | 12.6 | LO Del: 0→9.5 barg, Hdr: 0→6.8 barg, Tank: 0→84% |
| 2 | LO Pump B (Standby) | LOP-02 | START | 18.0 | 12.6 | Redundant — either pump satisfies permissive |
| 3 | Hydraulic Oil Pump A | HOP-01 | START | 16.0 | 11.2 | HO Press: 0→105 barg (two-stage ramp) |
| 4 | Encl Vent Fan 1 | EVF-01 | START | 4.0 | 2.8 | Enclosure ventilation established |
| 5 | Oil Mist Eliminator A | OME-01 | START | 3.0 | 2.1 | Oil mist extraction running |
| 6 | Jacking Oil Pump A | JOP-01 | START | 8.0 | 5.6 | Bearing lift-off oil active |
| 7 | Exhaust Frame Fan A | EFF-01 | START | 3.0 | 2.1 | Exhaust frame cooling |
| 8 | Seal Gas System | SGS-01 | START | 10.0 | 7.0 | Seal Press: 0→7 barg (N₂ primary/secondary) |
| 9 | ESDV Fuel Gas Valve | ESDV-FG | OPEN | 8.0 | 5.6 | FG Press: 0→32 barg, FG Temp: →58°C |

Note: Only one pump per system required (A or B). Parallel startup reduces total pre-start time. Equipment ramp times scale with Speed Multiplier.

# PERMISSIVE GATES

| GATE | COUNT | ITEMS |
| --- | --- | --- |
| TCS Startup Permit | 12 | LO pump RUN, LO del >5 barg, LO hdr >2.5 barg, LO tank >80%, LO filter DP normal, LO temp <65°C, ventilation RUN, OME RUN, vent DP normal, DCS permissive, F&G healthy, gas detection normal |
| Cranking Permit | 8 | LO pump RUN, LO del not low, LO hdr not low, HO pump RUN, HO >98 barg, LO tank >80%, JO active, FG temp normal |
| Ignition Permit | 6 | LO del not low, ESDV open, FG press ≥25 barg, seal gas active, HO not low, purge complete |
| Loading Permit | 4 | LO del not low, LO hdr not low, LO pump RUN, speed at FSNL (100%) |

# PHASE 2 — STARTUP SEQUENCE

| STEP | PHASE | NORMAL | DEMO | DESCRIPTION |
| --- | --- | --- | --- | --- |
| COMMON SEQUENCE (All Modes) |  |  |  |  |
| — | STANDBY | — | — | Verify all TCS permits: Startup → Cranking → Ignition → Loading |
| — | MODE SELECT | — | — | Select operating mode: CRANK / FIRE / AUTO / MANUAL / REMOTE |
| — | START COMMAND | — | — | Press START — requires Startup + Cranking permits satisfied |
| 10 | CRANKING | 15.0 | 10.5 | Speed: 0→1500 RPM (23%), TTXM: 24→28°C, FSR: 0→5% |
| 11 | PURGING | 20.0 | 14.0 | Stack ventilation at 1500 RPM, Purge timer 20s |
| 12 | PURGE HOLD* | — | — | If Ignition Permit not satisfied — holds until resolved |
| 13 | FIRING | 8.0 | 5.6 | Fuel admitted, spark igniters, TTXM: 28→260°C, flame detected |
| 14 | WARMUP | 12.0 | 8.4 | Speed hold at 1500 RPM, TTXM stabilizes ~200°C |
| FIRE MODE PATH (Stop at 50%, then select MAN/AUTO/REMOTE) |  |  |  |  |
| 15a | ACCEL → 50% | 18.0 | 12.6 | Speed: 1500→3300 RPM, TTXM→420°C, CPR→10:1 |
| 15b | FIRE HOLD (50%) | — | — | Operator selects MANUAL / AUTO / REMOTE to continue |
| 16 | ACCEL 50%→FSNL | 20.0 | 14.0 | Speed: 3300→6600 RPM, critical speed resonance at 5200 RPM |
| AUTO / MANUAL / REMOTE DIRECT PATH |  |  |  |  |
| 15 | ACCELERATION | 35.0 | 24.5 | Speed: 1500→6600 RPM, TTXM→550°C, CPR→21:1, IGV→100% |
| FSNL → BASE LOAD (All Modes) |  |  |  |  |
| 17 | FSNL | Hold | Hold | 6600 RPM / 100% speed, generator sync check, VIB analysis |
| — | LOAD COMMAND | — | — | Press LOAD — requires Loading Permit satisfied |
| 18 | LOADING | 55.0 | 38.5 | Load: 0→57 MW, TTXM→590°C, Exhaust spread monitoring |
| 19 | BASE LOAD | ∞ | ∞ | 57 MW steady-state, operator monitoring, fault response |

TOTAL SEQUENCE TIMING (START → BASE LOAD):

AUTO direct:   145s normal  |  101.5s demo

FIRE → AUTO:   148s normal + hold  |  103.6s demo + hold

# PHASE 3 — SHUTDOWN & COOLDOWN

| STEP | PHASE | NORMAL | DEMO | DESCRIPTION |
| --- | --- | --- | --- | --- |
| NORMAL SHUTDOWN |  |  |  |  |
| 20 | STOP COMMAND | — | — | Press STOP — initiates normal shutdown |
| 21 | SHUTDOWN | ~25 | ~17.5 | Load→0, speed ramp-down, flame out, coast through critical speeds |
| 22 | TURNING GEAR | Hold | Hold | 150 RPM shaft rotation, temps drifting, waiting for CD mode |
| — | SELECT COOLDOWN | — | — | Select COOLDOWN mode, press CD START |
| 23 | COOLDOWN ACTIVE | 60* | 42* | Forced cooling, WS temp: →<60°C (*or 36000s for real 10hr) |
| — | CD STOP | — | — | Operator releases unit when wheelspace <60°C |
| 24 | STANDBY | — | — | Unit on standby — ready for next startup |
| EMERGENCY TRIP |  |  |  |  |
| T1 | TRIP | Auto | Auto | VIB >5.5 mm/s OR LO <3 barg OR GB >80°C |
| T2 | TRIP COASTDOWN | ~10 | ~7 | Emergency fuel cutoff, speed decay, no load |
| T3 | TURNING GEAR | Hold | Hold | 150 RPM, same cooldown path as normal shutdown |

# INSTRUCTOR NOTES

• Speed Multiplier (1x/2x/5x/10x) scales all phase durations AND equipment ramp times globally.

• Demo Mode sets all phases to 70% of default duration (30% faster) for classroom demonstration.

• Individual phase timings are adjustable via the INSTRUCTOR tab without affecting other phases.

• Cooldown timer default is 60s (simulated). Set to 36000s for real 10-hour cooldown training.

• Fault injection available during running phases: VIB, LO, GB, FLAME, SURGE.

• Auto-trip triggers: Vibration >5.5 mm/s, LO Pressure <3 barg, Gearbox Temp >80 deg C.

• FIRE mode hold at 50% replicates VBA trainer behavior — operator must select next mode to continue.

• Wheelspace temperature must drop below 60 deg C before CD STOP is permitted.

GT-800E TCS-3000 State-Driven Turbine Trainer v3.1 — KURIAN GEORGE